## Sheet1
Warriner's DC Power Lead Calculator -- Copper Wire
1. | Enter your one way voltage drop |  | 0.125 | wire size |  | circular mils | ampacity
2. | Enter your one way lead length |  | 25 | 14 | = | 4110 | 15
3. | Enter your DC load in amperes |  | 400 | 12 | = | 6530 | 20
|  |  |  | 10 | = | 10380 | 30
0.1
| Calculated circular mils required |  | 888000 | 8 | = | 16510 | 45
|  |  |  | 6 | = | 26240 | 65
| Minimum required lead size (Ampacity must remain greater than fuse size. Choose next size if req'd.): |  |  | 4 | = | 41740 | 85
|  |  | 2-500MCM | 2 | = | 66360 | 115
|  |  |  | 0 | = | 105600 | 150
|  |  |  | 00 | = | 133100 | 175
|  |  |  | 0000 | = | 211600 | 230
| Actual one way voltage drop (This circuit, calculated from length used): |  |  | 350MCM | = | 350000 | 310
|  |  | 0.111 | 500MCM | = | 500000 | 380
|  |  |  | 750MCM | = | 750000 | 475
|  |  |  | 2-500MCM | = | 1000000 | 760
|  |  |  | 2-750MCM | = | 1500000 | 950
| Circular mils used for calculating the actual voltage drop in this circuit: |  |  | 3-750MCM | = | 2250000 | 1425
|  |  | 1000000 | 4-750MCM | = | 3000000 | 1900
|  |  |  | 5-750MCM | = | 3750000 | 2375
|  |  |  | 6-750MCM | = | 4500000 | 2850
|  |  |  | 7-750MCM | = | 5250000 | 3325
| Allowable Volt Drop = |  | 11.1 X AMPS X FT | 8-750MCM | = | 6000000 | 3800
|  |  | CM OF WIRE | 9-750MCM | = | 6750000 | 4275
|  |  |  | 10-750MCM | = | 7500000 | 4750
Special thanks to
1872 - 1984
Warriner's DC Power Lead Calculator © Vaughn S. Warriner 1/2006